CA DCIM (ecoMeter and VI) integration with MS AD / LDAP

Assumptions:

- MS AD is properly configured with a set of users which are members of an Active Directory Domain group and are associated to a MS AD company and a MS AD department.

- This document is not replacing the CA DCIM administrator manuals or Technical support troubleshooting checklists or good practices; the content on this document was created with the intention to share the experiences gained on the field after being successful with configuring the integration on site for some DCIM customers.

- If the steps mentioned on this document don’t work for your implementation, you should open a technical support ticket.

- Officially CA DCIM – VI supports only MS AD, but I was able to configure the integration using LDAP, so if your customer has LDAP and not MS AD you could still give it a try.

- The steps on this document were successfully executed in the following versions:

  - VI – 4.7.1, 4.8. and 4.10

  - ecoMeter 4.1, 4.3 and 44

Pre-configuration requisites

Before start configuring the integration in CA DCIM, you must get from MS AD – LDAP administrator the following information:

| MS AD / LDAP Information | Example |
| --- | --- |
| Server IP Address | 172.X.X.X |
| Service Port | 389 |
| Server Domain | corp.acmecorp.net |
| User \ password able to connect to the Server Domain which was selected to contain all members allowed to connect to DCIM-VI | Coyote777 \ roadrunner123 |
| Group or Groups Names where the DCIM Users are members of | acme_dcim_vi |
| Company for DCIM Users | ACME |
| Department for DCIM Users | Operations |

Chart No.1

Integration between VI and MS AD some details

How the integration works: The integration functionality works like this: Once the integration is set, when an user attempts to log in VI, instead of VI using its own security functionalities to allow or denied the user access, MS AD directly verifies If the typed user\password exists in MS AD, If so, the integration verifies if there is a company, a department, and a group set in VI similarly to those set and associated to the user just verified in MS AD. Additionally, if the user is logging in VI for the first time and is matching the mentioned criteria, but the user doesn’t exist in VI, the integration will create the user in VI, and then, the user will be allowed to log in VI. On the other hand, if the user exists in MS AD and in VI but the credential doesn’t match a message like “Username/password combination is not valid” is displayed on the login screen. Or if the user exists in MS AD as well as in VI but the Group, company or department defined in VI don’t match with the MS AD configured ones, messages such as “No Privilege...” or “Username/password combination is not valid” are displayed on the on the log in screen

Take into account that based on the integration’s logic VI administrators don’t longer need to administrate users creation\deletion, then, the New button under System  Users is displayed as disabled. BUT also take into account that the access control over the VI functionalities continues being managed in VI by the Groups privileges setting.

Warning: Once the integration is enabled, if disabling it all of the users in VI will be deleted BUT the admin user. (Enabling or disabling executing vdctools command line)

How to configure the integration from MS AD: This configuration is part of the MS AD administration tasks, users selected to be allowed to log in VI must be created in MS AD having associated to them a Company, a Department and being a member of an Active Directory Domain Group or Groups (one user can belong to more than one group) this is not an issue for VI meanwhile one of the groups where the user belong to is defined in VI. Don’t forget that the check box “change password in the next logon” must be turned OFF.

How to configure the integration from DCIM – VI Side: Once the users identified to connect in VI are created, those users must be associated to Company, Department, and must be members of the selected Domain Group or groups in MS AD, then, VI administrator must get those details from the MS AD administrator as well as the server information as suggested previously on this document. As preliminary activity, VI admin must execute the steps as follows in the VI Server to make sure the integration will successfully execute.

- Checking the Network and port connectivity from VI Server to MS Server.

  - Execute a Telnet from the VI server to the MS AD Server

  - Log is as root and execute the following command:

telnet IP_Address_of_MS_AD_server MS_AD_Port

Using the example information in chart No.1

telnet 172.X.X.X 389

telnet command should connect successfully. This will probe that the connection to the MS AD server is possible from the VI Server.

- Verifying If the selected User actually is successful authenticating in MS AD

  - Copy the attached tested.jar file to the directory /opt/VDC/jdk/bin/

  - Run the following command:

/opt/VDC/jdk/bin/java –jar tested.jar

  - Provided the required information that is prompted on the console. Using the example info as described in chart No.1

- Please enter the LDAP server IP: 172.X.X.X

- Please enter the LDAP service port: 389

- Please enter the LDAP server domain: corp.acmecorp.net

- Please enter the user name: Coyote777

- Please enter the user related password: roadrunner123

- NOTE: the password field is not encrypted. This is used only once and for kind of test.

- The script will then try to pass the provided parameters the same way the VI application does during login. If you get an output similar as what is displayed on the screenshot below, so you are all set, opposite if you get Java Errors you will need to review the configurations in MS AD.

- If no java errors, the output which is displayed on the screen could be concatenate to a text file, so you could search if the required users are being retrieving with the connection information you just used.

After being successful with these 2 tests (telnet and querying the MS AD users DB), you now are ready to configure VI.

- Log in VI Web Interface as the admin User

- Go to system tab and click on:

  - Company and create a New Company with the same name and spell as it is in MS AD

  - Departments  and create a New Department with the same name and spell as it is in MS AD

  - User Group  and create a New Group or Groups with the same name and spell as the Domain Groups which the selected users are member of in MS AD.

- As root, go to the VI Home Directory for example /opt/VDC/bin/vdctools

- Select option: 7) Enable Active Directory from the options list

  - From the example info content in chart No.1 above filling in the fields:

  - Enter Active Directory Server IP : 172.X.X.X

  - Enter Active Directory Port : 389

  - Enter Active Directory Server Domain : corp.acmecorp.net

- Log in VI Web Interface as the admin User, check the Company, Department and Group are created and set with the desired privileges.

- Log out

- Try log in with one of the desired VI users\

- User should be able to log in the web or 3D Client.

Some configurations Tips:

- If you are not sure about the company, department or groups for the users, that information is in MS AD, as showed on the screenshot below.

- VI Server Installation Guide states: “ Once a user is permitted to login to the application, the application will create/update mirrored user info in the application when necessary. The following Active Directory attributes are significant to the application: “ Use that table to understand the fields need to be populated for the users in MS AD or LDAP

- For MS AD or LDAP you can get/query information about groups and domains by executing tested.jar.

- The tested.jar file is very useful to troubleshoot the integration when users are not successfully log in VI.

- If after enabling the integration using the vdctools you disabled it, I noticed the user admin cannot login any more. To fix this just enable the integration again using vdctools command. Warning: Disabling the integration will delete all of the created users in VI.

- If after executing all of the steps as advised above your integration don’t work, there are 2 patches which are available via CA tech support. You should open a support ticket to get any of these patches.

- Note: I got these 2 patches after running the tested.jar and probe that integration wasn’t properly querying MS AD information, so the users couldn’t log in VI as MS AD wasn’t able to verify the userid and password at authentication moment. The patches information and issues numbers look like as follows: One is for 4.8.01(this ticket), and another is for 4.10(4.11). Please see below:

GRW-364-73830 [22000908 -01 - VI AD Integration issue] [4.8.01]  [Patch:150123.4801.GRW-364-73830.22000908.CAVIPatch.tar only for 4801]							      MBA-811-40393 [22048072-01: AD setup not working] [4.10] [Patch: 150129.4100.MBA-811-40393.22048072.CAVIPatch.tar for 4.10 and 4.11]

Integration between ecoMeter and MS AD

How the integration works: When an ecoMeter user attempts to log in ecoMeter the log in process verifies first if the user exits in the ecoMeter user’s base, If so, the user id and password are verified against the MS AD users base via the integration. If the user is no defined in ecoMeter, user is not able to log in although it is a valid user in MS AD. MS AD and ecoMeter integration works only to log in CA ecoMeter solution, if desired to have validation for the eHealth users against MS AD, a separated integration between eHealth and MS AD must be configured.

How to configure the integration from MS AD: This is part of the MS AD administration tasks, users selected to log in ecoMeter must be created in MS AD. The CA ecoMeter account name must be an exact match of the User Logon Name in Active Directory. In addition the check box “change password in the next logon” must be turned OFF

How to configure the integration from DCIM – ecoMeter Side: Tomcat is the one driving the integration. As mentioned initially on this document some important information about MS AD / LDAP settings will need to be known as this point.

- Select one MS AD user and is desired to log in ecoMeter using MS AD authentication.

- Get the password for that user ( in our example roadrunner123)

- If running an ecometer version older than ecoMeter 4.3 the user’s password needs to be typed in the file, it will be exposed as a text on the file.

- If running ecoMeter 4.3 apply the attached patch,

- if running ecoMeter 4.4 there is no need to apply the patch as the tool is included on the release itself.

- Either in 4.3 or 4.4, encrypt the password by executing the following:

  - Got to $ECOMETER_HOME/bin

  - ./ecoUtils -encrypt roadrunner123

  - The output of ecoUtils will display something like:

  - roadrunner123 -> 8A3A9EA1EF44D8D33FD3AE54C4BDD918

  - Copy the encrypted password and you need to insert that info into server.xml file

- Edit the file labeled as server.xml which lives in $ECOMETER_HOME/apache-tomcat/conf

- Search by the line <Realm which in comments (<!-- , )

- Uncomment that segment and using the MS AD/LDAP information collected initially, configure the integration, using our example organization ACME the segment looks like as follows:

<Realm className="org.apache.catalina.realm.CombinedRealm">

<Realm className=" com.ca.ecometer.secure.realm.EncryptedJNDIRealm "

connectionURL="ldap://corp.acmecorp.net:389"

connectionName="CN=Coyote Fox Coyote777,OU=Standard Users,OU=Users,OU=ACME,DC=corp,DC=acme,DC=net"

connectionPassword="8A3A9EA1EF44D8D33FD3AE54C4BDD918"

referrals="follow"

adCompat="true"

userBase="OU=Standard Users,OU=Users,OU=ACME,DC=corp,DC=acme,DC=net"

userSearch="(sAMAccountName={0})"

userSubtree="true"

roleBase="DC=corp,DC=acme,DC=net"

commonRole="user"

roleSubtree="true"

/>

<Realm className="org.apache.catalina.realm.DataSourceRealm"

dataSourceName="jdbc/ecomDB" userTable="emuser"

userNameCol="user_name" userCredCol="password"

userRoleTable="emuser_emrole" roleNameCol="role_name" />

</Realm>

Note:  The red values are the ones which change when configuring the integration in ecoMeter 4.3 and later versions. For previous versions that segment will look like as follows (note password is exposing as a text):

<Realm className="org.apache.catalina.realm.CombinedRealm">

<Realm className="org.apache.catalina.realm.JNDIRealm"

connectionURL="ldap://corp.acmecorp.net:389"

connectionName="CN=Coyote Fox Coyote777,OU=Standard Users,OU=Users,OU=ACME,DC=corp,DC=acme,DC=net"

connectionPassword="roadrunner123"

referrals="follow"

adCompat="true"

userBase="OU=Standard Users,OU=Users,OU=ACME,DC=corp,DC=acme,DC=net"

userSearch="(sAMAccountName={0})"

userSubtree="true"

roleBase="DC=corp,DC=acme,DC=net"

commonRole="user"

roleSubtree="true"

/>

<Realm className="org.apache.catalina.realm.DataSourceRealm"

dataSourceName="jdbc/ecomDB" userTable="emuser"

userNameCol="user_name" userCredCol="password"

userRoleTable="emuser_emrole" roleNameCol="role_name" />

</Realm>

- Stop and start ecoMeter tomcat services

- Execute ecoMeter web application and try log in with any of the MS AD desired users using the Domain password

User should log in ecoMeter Solution, getting all privileges defined by the ecoMeter administrator

References

The following documents are very useful when configuring the integration or when having issues configuring it or when attempting to understand how MS AD or LDAP work.

https://support.optimumpathinc.com/index.php/Knowledgebase/Article/View/14/21/active-directory-setup

https://support.optimumpathinc.com/index.php/Knowledgebase/Article/View/15/21/active-directory-troubleshooting

https://support.optimumpathinc.com/index.php/Knowledgebase/Article/View/138/21/active-directory-test-connection--user-authentication

https://support.optimumpathinc.com/index.php/Knowledgebase/Article/View/24/21/could-not-connect-to-the-active-directory-server

http://social.technet.microsoft.com/wiki/contents/articles/5392.active-directory-ldap-syntax-filters.aspx

https://technet.microsoft.com/en-us/library/cc725681.aspx

http://searchwindowsserver.techtarget.com/tutorial/Active-Directory-Tutorial